## Slide 1: Annex 68 - Subtask 4: Strategies for design and control of buildings Literature Review: Design strategies in UK
Maria del Carmen Bocanegra-Yanez, PhD Student, University of Strathclyde
maria.bocanegra-yanez@strath.ac.uk
15th March 2016

## Slide 2
1. Building Regulations
1.1. England and Wales
  Performance Criterion
  Ventilation strategies
  Ventilation systems
1.2. Scotland
  Ventilation strategies
  Ventilation systems
Literature Review: Design strategies in UK
2. Design Guides
2.1. CIBSE Guide A – Environmental design
2.2. Building Bulletin 101: ventilation for school buildings
3. References

## Slide 3
1. Building Regulations
1.1. England and Wales:
The building regulations in the UK are geared to prescriptive measures to ensure “adequate ventilation” but there are currently no mandatory standards covering IAQ with respect to specific CO2 levels or toxic pollutants (Sharpe et al. 2015). However, Appendix A for Approved Document F (HM Goverment 2010) does list a number of maximum exposures to particular pollutants.
Literature Review: Design strategies in UK
Indoor Air Pollutant | Performance Criterion
Moisture | There should be no visible mould on external walls in a properly heated dwelling with typical moisture generation.
NO2 | Limit exposure level: 288 µg/m3 (150 ppb) – 1 hour average 40 µg/m3 (20 ppb) – long-term average
CO | Limit exposure level: 100 mg/ m3 (90 ppm) – 15 minute averaging time 60 mg/ m3 (50 ppm) – 30 minute averaging time 30 mg/ m3 (25 ppm) – 1 hour averaging time 10 mg/ m3 (10 ppm) – 8 hours averaging time
TVOC | Limit exposure level: 300 µg/m3 – 8 hours average

## Slide 4
Approved Document F (HM Goverment 2010) adopts the following strategies:
Extract ventilation either intermittent or continuous.
Whole building/dwelling ventilation provides continuous air exchange.
Purge ventilation to aid the removal of high concentrations of pollutants and water vapour released from occasional activities such as painting and decorating or accidental releases such as smoke from burnt food or spillage of water. It is intermittent. There is guidance in AD-F for the dimension of opening windows so as to allow for purge ventilation at a rate of 4 air changes/hour (ach).
Literature Review: Design strategies in UK

## Slide 5
There are four different ventilation systems for dwellings without basements within the UK building regulations:
1. Background ventilators and intermittent extract fans
2. Passive stack ventilation (PSV)
3. Continuous mechanical extract (MEV)
4. Continuous mechanical supply and extract with heat recovery (MVHR)
Literature Review: Design strategies in UK

## Slide 6
According to a BSRIA survey of dwellings constructed in 2011 to the 2010 Part F requirements, approximately equal numbers of dwellings used systems 1, 3, and 4, with less than 1% using system 2 (Adam-Smith 2014).
Mechanical extract ventilation with trickle vents is by far the most common ventilation strategy in the UK but with a focus on lower energy buildings there is a move towards mechanical ventilation with heat recovery (Adam-Smith 2014).
Other types of ventilation systems, such as demand controlled ventilation (DCV) and positive input ventilation (PIV) are allowed to be used in the UK. These systems must be shown to achieve certain performance criteria (Knights & Gilbert 2015).
Literature Review: Design strategies in UK

## Slide 7
1.2. Scotland
According to the Scottish Building Standards 2015 (The Scottish Government 2015b), there are three ventilation strategies:
Natural Ventilation
Mechanical Ventilation
Combined Natural and Mechanical Ventilation
These strategies can be implemented by the following ventilation systems (The Scottish Government 2015a):
Natural ventilation – windows, doors and trickle ventilators
Natural Ventilation - Passive stack ventilators
Mechanical extract – intermittent extract fans
Mechanical Ventilation – decentralised mechanical extract ventilation (dMEV)
Mechanical Ventilation - centralised mechanical extract ventilation (MEV)
Mechanical Ventilation – continuously balanced supply and extract ventilation (with or without heat recovery).
Literature Review: Design strategies in UK

## Slide 8
2. Design Guides
2.1. CIBSE Guide A – Environmental design (The Chartered Institution Building Services Engineers London 2006)
It summarizes the fundamentals of the ventilation techniques as follows:
• Natural ventilation:
  Wind effect
  Stack effect
• Mechanical ventilation:
  Supply-only ventilation
  Extract-only ventilation
  Balanced mechanical ventilation
• Mixed mode ventilation:
  Supplementary: mechanical ventilation is applied when natural driving forces are inadequate to meet ventilation need.
  Complementary: natural and mechanical ventilation work together to meet the ventilation needs of a building.
  Alternate: both natural and mechanical ventilation systems are separately incorporated into the building. The actual system used at any time is dependent on current climate conditions and ventilation need.
Literature Review: Design strategies in UK

## Slide 9
2.2. Building Bulletin 101: ventilation for school buildings (Education Funding Agency 2014)
It is intended to give information about ventilation for school buildings, which has received more attention than dwellings.
Ventilation strategies include:
• Natural ventilation
• Hybrid ventilation
• Mechanical ventilation
• Local ventilation
Natural ventilation design receives more attention with one chapter focusing on design guidance and another one focusing on the ClassVent calculator, which provides a means of sizing ventilation openings for natural ventilation design.
Literature Review: Design strategies in UK

## Slide 10
3. References
Adam-Smith, B., 2014. Avoiding the Risks of Poor Ventilation. Available at: http://www.houseplanninghelp.com/wp-content/uploads/2014/03/Mark-Siddall.pdf.
Education Funding Agency, 2014. Building Bulletin 101 Ventilation of School Buildings, Available at: https://www.gov.uk/government/publications/building-bulletin-101-ventilation-for-school-buildings.
HM Goverment, 2010. The Building Regulations 2010 Ventilation APPROVED DOCUMENT F,
Knights, C. & Gilbert, A., 2015. A BSRIA Guide. Domestic Ventilation Systems.
Sharpe, T. et al., 2015. Occupant Interactions and Effectiveness of Natural Ventilation Strategies in Contemporary New Housing in Scotland, UK. International Journal of Environmental Research and Public Health, 12(7), pp.8480–8497. Available at: http://www.mdpi.com/1660-4601/12/7/8480/.
The Chartered Institution Building Services Engineers London, 2006. Environmental Design. CIBSE Guide A.
The Scottish Government, 2015a. BUILDING STANDARDS SUPPORTING GUIDANCE DOMESTIC VENTILATION, Available at: http://www.gov.scot/Resource/0049/00490250.pdf.
The Scottish Government, 2015b. Technical Handbook, Available at: http://www.gov.scot/Topics/Built-Environment/Building/Building-standards/publications/pubtech/th2015domcomp.
Literature Review: Design strategies in UK

## Slide 11
Literature Review: Design strategies in UK